## Wires
Wire Number | End A | End B | Length | Type |  | Signal
101 | CB-1 | 206 | 20 | 18ga | BLK | 120-L
102 | BAT-120-L | 207 | 12 | * |  | 120-L | *2-wire power
103 | BAT-120-N | 209 | 12 | * |  | 120-N | *2-wire power
104 | 213 | 208 | 11 | 18ga | WHT | 120-L
105 | 107 | PS-L | 6.5 | 18ga | BLK | 120-L
106 | 108 | PS-N | 6 | 18ga | WHT | 120-N
107 | 210 | PS-GND | 11.5 | 18ga | GRN | GND
108 | 211 | 101 | 20 | 18ga | GRN | GND
109 | BAT-5-POS | 104 | 17 | * |  | 5VDC | *2-wire barrel
110 | BAT-5-NEG | 103 | 17 | * |  | GND | *2-wire barrel
111 | PS-NEG | 102 | 13.5 | 20ga | BLU | GND | **DOUBLE
112 | PL-GND | 102 | 8 | 20ga | BLU | GND | **DOUBLE
113 | PS-POS | 237 | 26 | 20ga | BLU | 24VDC | **DOUBLE
114 | T3-PWR-POS | 237 | 4 | 20ga | BLU | 24VDC | **DOUBLE
115 | T3-PWR-GND | 212 | 11 | 20ga | BLU | GND | **DOUBLE
116 | 105 | PL-5V | 8.5 | 20ga | BLU | 5VDC
117 | T3-485-GND | PL-485-GND | 5 | 20ga | BLU | RS485-GND
118 | T3-485A | PL-485A | 5 | 20ga | BLU | RS485A
119 | T3-485B | PL-485B | 5 | 20ga | BLU | RS485B
120 | 236 | 131L | 5 | 20ga | BLU | 24VDC | **DOUBLE
121 | 131L | 130L | 3.5 | 20ga | BLU | 24VDC | **DOUBLE
122 | 130L | 129L | 3.5 | 20ga | BLU | 24VDC | **DOUBLE
123 | 129L | 128L | 3.5 | 20ga | BLU | 24VDC | **DOUBLE
124 | 128L | 127L | 3.5 | 20ga | BLU | 24VDC | **DOUBLE
125 | 127L | 126L | 3.5 | 20ga | BLU | 24VDC | **DOUBLE
126 | T3-485B | 225 | 6.5 | 20ga | BLU | RS485B | **DOUBLE
127 | 225 | 222 | 5.5 | 20ga | BLU | RS485B | **DOUBLE
128 | 222 | 219 | 5.5 | 20ga | BLU | RS485B | **DOUBLE
129 | 219 | 216 | 5.5 | 20ga | BLU | RS485B | **DOUBLE
130 | T3-485A | 224 | 6.5 | 20ga | BLU | RS485A | **DOUBLE
131 | 224 | 221 | 5.5 | 20ga | BLU | RS485A | **DOUBLE
132 | 221 | 218 | 5.5 | 20ga | BLU | RS485A | **DOUBLE
133 | 218 | 215 | 5.5 | 20ga | BLU | RS485A | **DOUBLE
134 | T3-485-GND | 223 | 6.5 | 20ga | BLU | RS485-GND | **DOUBLE
135 | 223 | 220 | 5.5 | 20ga | BLU | RS485-GND | **DOUBLE
136 | 220 | 217 | 5.5 | 20ga | BLU | RS485-GND | **DOUBLE
137 | 217 | 214 | 5.5 | 20ga | BLU | RS485-GND | **DOUBLE
138 | 212 | T3-1L | 8.5 | 20ga | BLU | GND | **DOUBLE
139 | T3-1L | T3-2L | 3 | 20ga | BLU | GND | **DOUBLE
140 | T3-2L | T3-3L | 3 | 20ga | BLU | GND | **DOUBLE
141 | T3-3L | T3-4L | 3 | 20ga | BLU | GND | **DOUBLE
142 | T3-4L | T3-5L | 3 | 20ga | BLU | GND | **DOUBLE
143 | T3-5L | T3-6L | 3 | 20ga | BLU | GND | **DOUBLE
144 | T3-1U | 226U | 5.5 | 20ga | BLU | 4-20mA
145 | T3-2U | 227U | 5.5 | 20ga | BLU | 4-20mA
146 | T3-3U | 228U | 5.5 | 20ga | BLU | 4-20mA
147 | T3-4U | 229U | 5.5 | 20ga | BLU | 4-20mA
148 | T3-5U | 230U | 5.5 | 20ga | BLU | 4-20mA
149 | T3-6U | 231U | 5.5 | 20ga | BLU | 4-20mA
150 | T3-7L | 232L | 3.5 | 20ga | BLU | dry contact
151 | T3-8L | 233L | 3.5 | 20ga | BLU | dry contact
152 | T3-9L | 234L | 3.5 | 20ga | BLU | dry contact
153 | T3-10L | 235L | 3.5 | 20ga | BLU | dry contact
154 | T3-7U | 232U | 5.5 | 20ga | BLU | dry contact
155 | T3-8U | 233U | 5.5 | 20ga | BLU | dry contact
156 | T3-9U | 234U | 5.5 | 20ga | BLU | dry contact
157 | T3-10U | 235U | 5.5 | 20ga | BLU | dry contact
158 | 106 | CT-VOLTS-POS | 14 | 20ga | BLU | 120L
159 | 109 | CT-VOLTS-NEG | 14 | 20ga | BLU | 120N
160 | 216 | CT-RS485-NEG | 17 | 20ga | BLU | RS485B | **DOUBLE
161 | 215 | CT-RS405-POS | 17 | 20ga | BLU | RS485A | **DOUBLE
162 | 214 | CT-PWR-GND | 17 | 20ga | BLU | GND | **DOUBLE
163 | 238 | CT-PWR-POS | 25 | 20ga | BLU | 24VDC
R1 | PL-485A | PL-485B |  |  |  |  | 120-ohm resistor
As-Built
3 | DN-2J4Y
3 | DN-3J2Y

## BOM
Enclosure Bill of Materials
Qty | Item | Part # | Vendor | Link | Notes
1 | Project Lab | ProjectLab v3.e | Wilderness Labs
1 | Project Lab Enclosure | n/a | Wilderness Labs
1 | EG21 Mikrobus | ED2x v1.c | Wilderness Labs
1 | Enclosure with Backplane |  | Amazon | https://amzn.to/40jyGSg | 20"×16.1"×7.9"
2 | DIN rail |  | Automation direct |  | 8"
1 | DIN rail |  | Automation direct |  | 10.5"
1 | wire duct | T1E-1015G-1 | Automation direct | https://www.automationdirect.com/adc/shopping/catalog/wiring_solutions/wire_duct/narrow_finger_wall/t1e-1015g-1 | 1" wide, 1.5" high, 12" long
2 | wire duct | T1E-1015G-1 | Automation direct | https://www.automationdirect.com/adc/shopping/catalog/wiring_solutions/wire_duct/narrow_finger_wall/t1e-1015g-1 | 1" wide, 1.5" high, 10" long
1 | Modbus I/O | T3E-22i | Temco controls | https://temcocontrols.com/shop/bacnet-modbus-modules/
1 | Power meter | SPM1-50-AC | Temco controls | https://temcocontrols.com/shop/single-phase-power-meterwith-internal-ct/
1 | 24V power supply | PSB24-060S-P | Automation direct | https://www.automationdirect.com/adc/shopping/catalog/power_products_(electrical)/dc_power_supplies/din_rail_mount/psb24-060s-p
1 | UPS Battery/power supply |  | Amazon | https://amzn.to/4ekEJfi
1 | Battery holder |  | Wilderness Labs |  | self-print
2 | Velcro strips |  | Amazon | https://amzn.to/4kioRLO
1 | Circuit breaker | FAZ-C5-1-SP | Automation Direct |  | 5A
10 | Green terminal block | KN-T12GRN | Automation Direct
17 | Blue terminal block | KN-T12BLU | Automation Direct
1 | Yellow terminal block | KN-T12YEL | Automation Direct
4 | Terminal block separator | KN-ST1GRY | Automation Direct
9 | Terminal block end stop | KN-EB7 | Automation Direct
10 | Blue terminal block - 2-level | KN-D12BLU | Automation Direct
1 | Terminal block separator - 2-level | KN-ECDGRY | Automation Direct
3 | Terminal block jumpers - 2-pos | KN-2J12 | Automation Direct | https://www.automationdirect.com/adc/shopping/catalog/wiring_solutions/terminal_blocks/jumpers/kn-2j12
3 | Terminal block jumpers - 3-pos | KN-3J12 | Automation Direct | https://www.automationdirect.com/adc/shopping/catalog/wiring_solutions/terminal_blocks/jumpers/kn-3j12
| Wire markers | KN-L5-101-150-250 | Automation Direct
| Wire markers | KN-L5-201-250-250 | Automation Direct
| Ferrules |  | Amazon | https://amzn.to/3TDDqhU | 16awg
| Ferrules |  | Amazon | https://amzn.to/4kXRjDD | 20awg
| Twin ferrules |  | Amazon | https://amzn.to/4kSjP9L | 20awg, 2-wire
13 | Truss screws | #8 x 1/2" | Amazon | https://amzn.to/44ioFpw
1 | Terminating resistor |  |  |  | 120-ohm, through-hole

## Sheet1
FIELD WIRING
112 | 120-GND
113 | 120-N
CB-2 | 120-L
114 | RS485 GND
115 | RS485 A
116 | RS485 B
117 | RS485 GND
118 | RS485 A
119 | RS485 B
120 | RS485 GND
121 | RS485 A
122 | RS485 B
123 | RS485 GND
124 | RS485 A
125 | RS485 B
126U | 4-20mA (-)
126L | 4-20mA (+) [24VDC]
127U | 4-20mA (-)
127L | 4-20mA (+) [24VDC]
128U | 4-20mA (-)
128L | 4-20mA (+) [24VDC]
129U | 4-20mA (-)
129L | 4-20mA (+) [24VDC]
130U | 4-20mA (-)
130L | 4-20mA (+) [24VDC]
131U | 4-20mA (-)
131L | 4-20mA (+) [24VDC]
132U | Dry Contact A
132L | Dry Contact B
133U | Dry Contact A
133L | Dry Contact B
134U | Dry Contact A
134L | Dry Contact B
135U | Dry Contact A
135L | Dry Contact B
136 | 24VDC
137 | 24VDC
138 | 24VDC